## System Data
Component | Parameter | Value
PV (3-phase) | Capacity | 300 kW
PV (1-phase) | Capacity | 100 kW
Wind Turbine | Capacity | 500 kW
Diesel Gen | Capacity | 300 kW
BESS | Power Capacity | 100 kW
BESS | Energy Capacity | 1000 kWh
BESS | Charging Efficiency | ηC (unspecified)
BESS | Discharging Eff. | ηD (unspecified)
Electricity Price | Buy (off-peak 11PM - 6AM) | $0.08/kWh
Electricity Price | Buy (peak) | $0.10/kWh
Electricity Price | Sell | $0.04/kWh
PV and Wind Error | Gaussian (mean = 0, SD = 10% of predicted)
Load Error | Gaussian (mean = 0, SD = 5% of nominal load)

## Load Data
Loads
Node |  | Load | Ph-1
|  | Model | kW | kVAr
MG1 | 1 | Y-Z | 40 | 20
MG1 | 2 | Y-PQ | 40 | 20
MG1 | 4 | Y-I | 40 | 20
MG1 | 7 | Y-PQ | 20 | 10
MG1 | 8 | Y-PQ | 20 | 10
MG1 | 10 | Y-I | 40 | 20
MG1 | 12 | Y-PQ | 40 | 20
MG1 | 14 | Y-Z | 40 | 20
MG1 | 16 | Y-PQ | 40 | 20
MG1 | 17 | Y-I | 40 | 20
MG1 | 19 | D-PQ | 40 | 20
MG1 | 21 | Y-PQ | 20 | 10
MG1 | 22 | Y-PQ | 20 | 10
MG1 | 23 | Y-Z | 40 | 20
MG1 | 25 | Y-I | 20 | 10
MG1 | 26 | Y-PQ | 20 | 10
MG1 | 27 | Y-I | 35 | 25
MG1 | 28 | Y-Z | 70 | 50
MG1 | 29 | Y-PQ | 35 | 25
MG1 | 30 | Y-PQ | 40 | 20
MG1 | 31 | Y-PQ | 20 | 10
MG1 | 34 | Y-Z | 40 | 20
MG1 | 35 | Y-I | 20 | 10
MG1 | 36 | Y-PQ | 20 | 10
MG2 | 1 | Y-PQ | 0 | 20
MG2 | 2 | Y-PQ | 40 | 20
MG2 | 4 | Y-PQ | 20 | 10
MG2 | 5 | Y-PQ | 40 | 20
MG2 | 6 | Y-PQ | 40 | 20
MG2 | 8 | Y-Z | 40 | 20
MG2 | 9 | Y-PQ | 40 | 20
MG2 | 10 | D-I | 105 | 80
MG2 | 12 | Y-PQ | 40 | 20
MG2 | 13 | Y-Z | 40 | 20
MG2 | 14 | Y-PQ | 40 | 20
MG2 | 16 | Y-PQ | 20 | 10
MG2 | 17 | Y-PQ | 40 | 20
MG2 | 18 | Y-PQ | 20 | 10
MG2 | 19 | Y-PQ | 40 | 20
MG2 | 20 | Y-PQ | 20 | 10
MG2 | 21 | Y-PQ | 40 | 20
MG2 | 22 | Y-PQ | 40 | 20
MG2 | 24 | Y-I | 40 | 20
MG2 | 26 | Y-PQ | 40 | 20
MG2 | 28 | Y-PQ | 40 | 20
MG2 | 29 | Y-PQ | 20 | 10
MG2 | 30 | Y-PQ | 20 | 10
MG3 | 3 | Y-PQ | 40 | 20
MG3 | 5 | Y-PQ | 20 | 10
MG3 | 6 | Y-I | 20 | 10
MG3 | 7 | Y-Z | 40 | 20
MG3 | 8 | Y-PQ | 20 | 10
MG3 | 10 | Y-PQ | 40 | 40
MG3 | 11 | Y-PQ | 40 | 40
MG3 | 13 | Y-PQ | 20 | 10
MG3 | 14 | Y-PQ | 40 | 40
MG3 | 15 | Y-PQ | 40 | 40
MG3 | 18 | Y-PQ | 40 | 20
MG3 | 19 | Y-PQ | 40 | 20
MG3 | 20 | Y-Z | 40 | 20
MG4 | 1 | Y-PQ | 40 | 20
MG4 | 3 | Y-I | 20 | 10
MG4 | 4 | Y-Z | 40 | 20
MG4 | 5 | Y-PR | 40 | 20
MG4 | 6 | Y-PQ | 20 | 10
MG4 | 7 | Y-PQ | 20 | 10
MG4 | 9 | Y-PQ | 20 | 10
MG4 | 10 | Y-PQ | 40 | 20
MG4 | 12 | Y-Z | 40 | 20
MG4 | 13 | Y-I | 20 | 10
MG4 | 15 | Y-Z | 40 | 20
MG4 | 17 | Y-PQ | 20 | 10
MG4 | 18 | Y-PQ | 40 | 20
MG4 | 20 | Y-PQ | 40 | 20
MG4 | 21 | Y-PQ | 40 | 20
MG4 | 23 | Y-Z | 20 | 10
MG4 | 24 | Y-PQ | 20 | 10
MG4 | 26 | Y-I | 20 | 10
MG4 | 27 | Y-PQ | 20 | 10
MG4 | 28 | Y-PQ | 20 | 10
MG4 | 29 | Y-Z | 40 | 20
MG4 | 30 | Y-PQ | 40 | 20
MG4 | 31 | Y-I | 75 | 35
MG4 | 32 | D-Z | 35 | 25
MG4 | 33 | Y-PQ | 75 | 35
Total |  |  | 2910 | 1615

## Line Data
Line Segment Data
Node A |  | Node B |  | Length (ft) | Mile | Config | Raa+jXaa
MG1 | 1 | MG1 | 2 | 350 | 0.066288 | 2 | 0.4666 + j1.0482
MG1 | 4 | MG1 | 1 | 300 | 0.056818 | 2 | 0.4666 + j1.0482
MG1 | 2 | MG1 | 3 | 200 | 0.037879 | 2 | 0.4666 + j1.0482
MG1 | 5 | MG1 | 4 | 200 | 0.037879 | 2 | 0.4666 + j1.0482
MG1 | 5 | MG1 | 6 | 350 | 0.066288 | 7 | 0.4576 + j1.078
MG1 | 11 | MG1 | 5 | 275 | 0.052083 | 2 | 0.4666 + j1.0482
MG1 | 6 | MG1 | 9 | 275 | 0.052083 | 7 | 0.4576 + j1.078
MG1 | 6 | MG1 | 7 | 225 | 0.042614 | 11 | 1.3292 + j1.3475
MG1 | 7 | MG1 | 8 | 300 | 0.056818 | 11 | 1.3292 + j1.3475
MG1 | 9 | MG1 | 10 | 500 | 0.094697 | 9 | 1.3292 + j1.3475
MG1 | 11 | MG1 | 12 | 550 | 0.10417 | 11 | 1.3292 + j1.3475
MG1 | 13 | MG1 | 11 | 250 | 0.047348 | 2 | 0.4666 + j1.0482
MG1 | 13 | MG1 | 14 | 525 | 0.099432 | 10 | 1.3292 + j1.3475
MG1 | 15 | MG1 | 13 | 300 | 0.056818 | 2 | 0.4666 + j1.0482
MG1 | 15 | MG1 | 16 | 250 | 0.047348 | 9 | 1.3292 + j1.3475
MG1 | 15 | MG1 | 18 | 300 | 0.056818 | 2 | 0.4666 + j1.0482
MG1 | 16 | MG1 | 17 | 325 | 0.061553 | 9 | 1.3292 + j1.3475
MG1 | 18 | MG1 | 19 | 375 | 0.071023 | 4 | 0.4615 + j1.0651
MG1 | 19 | MG1 | 33 | 650 | 0.12311 | 8 | 0.4576 + j1.078
MG1 | 19 | MG1 | 20 | 250 | 0.047348 | 1 | 0.4576 + j1.078
MG1 | 20 | MG1 | 21 | 325 | 0.061553 | 11 | 1.3292 + j1.3475
MG1 | 20 | MG1 | 22 | 250 | 0.047348 | 1 | 0.4576 + j1.078
MG1 | 22 | MG1 | 23 | 500 | 0.094697 | 10 | 1.3292 + j1.3475
MG1 | 22 | MG1 | 24 | 200 | 0.037879 | 1 | 0.4576 + j1.078
MG1 | 24 | MG1 | 25 | 200 | 0.037879 | 9 | 1.3292 + j1.3475
MG1 | 24 | MG1 | 27 | 250 | 0.047348 | 1 | 0.4576 + j1.078
MG1 | 25 | MG1 | 26 | 300 | 0.056818 | 9 | 1.3292 + j1.3475
MG1 | 27 | MG1 | 28 | 150 | 0.028409 | 4 | 0.4615 + j1.0651
MG1 | 27 | MG1 | 29 | 250 | 0.047348 | 4 | 0.4615 + j1.0651
MG1 | 29 | MG1 | 30 | 250 | 0.047348 | 4 | 0.4615 + j1.0651
MG1 | 30 | MG1 | 31 | 250 | 0.047348 | 4 | 0.4615 + j1.0651
MG1 | 31 | MG1 | 32 | 500 | 0.094697 | 4 | 0.4615 + j1.0651
MG1 | 33 | MG1 | 34 | 300 | 0.056818 | 9 | 1.3292 + j1.3475
MG1 | 33 | MG1 | 35 | 250 | 0.047348 | 10 | 1.3292 + j1.3475
MG1 | 35 | MG1 | 36 | 325 | 0.061553 | 10 | 1.3292 + j1.3475
MG2 | 2 | MG2 | 1 | 250 | 0.047348 | 6 | 0.4576 + j1.078
MG2 | 3 | MG2 | 2 | 250 | 0.047348 | 6 | 0.4576 + j1.078
MG2 | 3 | MG2 | 4 | 675 | 0.12784 | 11 | 1.3292 + j1.3475
MG2 | 6 | MG2 | 3 | 475 | 0.089962 | 6 | 0.4576 + j1.078
MG2 | 4 | MG2 | 5 | 475 | 0.089962 | 11 | 1.3292 + j1.3475
MG2 | 7 | MG2 | 6 | 475 | 0.089962 | 6 | 0.4576 + j1.078
MG2 | 7 | MG2 | 8 | 225 | 0.042614 | 6 | 0.4576 + j1.078
MG2 | 9 | MG2 | 7 | 100 | 0.018939 | 6 | 0.4576 + j1.078
MG2 | 10 | MG2 | 9 | 400 | 0.075758 | 6 | 0.4576 + j1.078
MG2 | 10 | MG2 | 20 | 700 | 0.13258 | 3 | 0.4615 + j1.0651
MG2 | 11 | MG2 | 10 | 200 | 0.037879 | 3 | 0.4615 + j1.0651
MG2 | 11 | MG2 | 12 | 275 | 0.052083 | 11 | 1.3292 + j1.3475
MG2 | 15 | MG2 | 11 | 275 | 0.052083 | 3 | 0.4615 + j1.0651
MG2 | 12 | MG2 | 13 | 350 | 0.066288 | 11 | 1.3292 + j1.3475
MG2 | 13 | MG2 | 14 | 400 | 0.075758 | 11 | 1.3292 + j1.3475
MG2 | 15 | MG2 | 16 | 200 | 0.037879 | 9 | 1.3292 + j1.3475
MG2 | 15 | MG3 | 17 | 250 | 0.047348 | 3 | 0.4615 + j1.0651
MG2 | 16 | MG2 | 17 | 275 | 0.052083 | 9 | 1.3292 + j1.3475
MG2 | 17 | MG2 | 18 | 325 | 0.061553 | 9 | 1.3292 + j1.3475
MG2 | 18 | MG2 | 19 | 275 | 0.052083 | 9 | 1.3292 + j1.3475
MG2 | 20 | MG2 | 21 | 450 | 0.085227 | 6 | 0.4576 + j1.078
MG2 | 21 | MG2 | 22 | 175 | 0.033144 | 9 | 1.3292 + j1.3475
MG2 | 21 | MG2 | 23 | 275 | 0.052083 | 6 | 0.4576 + j1.078
MG2 | 23 | MG2 | 24 | 225 | 0.042614 | 10 | 1.3292 + j1.3475
MG2 | 23 | MG2 | 25 | 225 | 0.042614 | 6 | 0.4576 + j1.078
MG2 | 25 | MG2 | 26 | 300 | 0.056818 | 11 | 1.3292 + j1.3475
MG2 | 25 | MG2 | 27 | 225 | 0.042614 | 6 | 0.4576 + j1.078
MG2 | 27 | MG2 | 28 | 275 | 0.052083 | 9 | 1.3292 + j1.3475
MG2 | 27 | MG2 | 29 | 300 | 0.056818 | 6 | 0.4576 + j1.078
MG2 | 29 | MG2 | 30 | 200 | 0.037879 | 10 | 1.3292 + j1.3475
MG3 | 2 | MG3 | 1 | 1000 | 0.18939 | 3 | 0.4615 + j1.0651
MG3 | 2 | MG3 | 3 | 450 | 0.085227 | 9 | 1.3292 + j1.3475
MG3 | 9 | MG3 | 2 | 325 | 0.061553 | 3 | 0.4615 + j1.0651
MG3 | 3 | MG3 | 4 | 300 | 0.056818 | 9 | 1.3292 + j1.3475
MG3 | 4 | MG3 | 5 | 575 | 0.1089 | 9 | 1.3292 + j1.3475
MG3 | 4 | MG3 | 6 | 125 | 0.023674 | 9 | 1.3292 + j1.3475
MG3 | 6 | MG3 | 7 | 525 | 0.099432 | 9 | 1.3292 + j1.3475
MG3 | 7 | MG3 | 8 | 325 | 0.061553 | 9 | 1.3292 + j1.3475
MG3 | 9 | MG3 | 10 | 225 | 0.042614 | 10 | 1.3292 + j1.3475
MG3 | 12 | MG3 | 9 | 275 | 0.052083 | 3 | 0.4615 + j1.0651
MG3 | 10 | MG3 | 11 | 575 | 0.1089 | 10 | 1.3292 + j1.3475
MG3 | 12 | MG3 | 13 | 225 | 0.042614 | 11 | 1.3292 + j1.3475
MG3 | 16 | MG3 | 12 | 250 | 0.047348 | 3 | 0.4615 + j1.0651
MG3 | 13 | MG3 | 14 | 325 | 0.061553 | 11 | 1.3292 + j1.3475
MG3 | 14 | MG3 | 15 | 700 | 0.13258 | 11 | 1.3292 + j1.3475
MG3 | 17 | MG3 | 18 | 275 | 0.052083 | 3 | 0.4615 + j1.0651
MG3 | 18 | MG3 | 19 | 550 | 0.10417 | 3 | 0.4615 + j1.0651
MG3 | 19 | MG3 | 20 | 300 | 0.056818 | 3 | 0.4615 + j1.0651
MG3 | 20 | MG3 | 21 | 800 | 0.15152 | 3 | 0.4615 + j1.0651
MG4 | 0 | MG4 | 1 | 400 | 0.075758 | 1 | 0.4576 + j1.078
MG4 | 1 | MG4 | 6 | 175 | 0.033144 | 10 | 1.3292 + j1.3475
MG4 | 1 | MG4 | 2 | 250 | 0.047348 | 11 | 1.3292 + j1.3475
MG4 | 1 | MG4 | 7 | 300 | 0.056818 | 1 | 0.4576 + j1.078
MG4 | 2 | MG4 | 5 | 200 | 0.037879 | 11 | 1.3292 + j1.3475
MG4 | 2 | MG4 | 3 | 325 | 0.061553 | 11 | 1.3292 + j1.3475
MG4 | 3 | MG4 | 4 | 250 | 0.047348 | 11 | 1.3292 + j1.3475
MG4 | 7 | MG4 | 8 | 200 | 0.037879 | 1 | 0.4576 + j1.078
MG4 | 8 | MG4 | 9 | 225 | 0.042614 | 10 | 1.3292 + j1.3475
MG4 | 8 | MG4 | 10 | 225 | 0.042614 | 9 | 1.3292 + j1.3475
MG4 | 8 | MG4 | 14 | 300 | 0.056818 | 1 | 0.4576 + j1.078
MG4 | 10 | MG4 | 11 | 425 | 0.080492 | 9 | 1.3292 + j1.3475
MG4 | 11 | MG4 | 12 | 250 | 0.047348 | 9 | 1.3292 + j1.3475
MG4 | 11 | MG4 | 13 | 250 | 0.047348 | 9 | 1.3292 + j1.3475
MG4 | 14 | MG4 | 15 | 150 | 0.028409 | 11 | 1.3292 + j1.3475
MG4 | 14 | MG1 | 15 | 825 | 0.15625 | 2 | 0.4666 + j1.0482
MG4 | 15 | MG4 | 16 | 100 | 0.018939 | 11 | 1.3292 + j1.3475
MG4 | 35 | MG2 | 15 | 350 | 0.066288 | 6 | 0.4576 + j1.078
MG4 | 16 | MG4 | 18 | 375 | 0.071023 | 11 | 1.3292 + j1.3475
MG4 | 16 | MG4 | 17 | 350 | 0.066288 | 11 | 1.3292 + j1.3475
MG4 | 19 | MG4 | 20 | 400 | 0.075758 | 1 | 0.4576 + j1.078
MG4 | 20 | MG4 | 21 | 200 | 0.037879 | 1 | 0.4576 + j1.078
MG4 | 21 | MG4 | 22 | 125 | 0.023674 | 1 | 0.4576 + j1.078
MG4 | 22 | MG4 | 23 | 275 | 0.052083 | 1 | 0.4576 + j1.078
MG4 | 22 | MG4 | 25 | 350 | 0.066288 | 3 | 0.4615 + j1.0651
MG4 | 23 | MG4 | 24 | 275 | 0.052083 | 1 | 0.4576 + j1.078
MG4 | 25 | MG4 | 26 | 250 | 0.047348 | 10 | 1.3292 + j1.3475
MG4 | 25 | MG4 | 28 | 750 | 0.14205 | 3 | 0.4615 + j1.0651
MG4 | 26 | MG4 | 27 | 250 | 0.047348 | 10 | 1.3292 + j1.3475
MG4 | 28 | MG4 | 34 | 550 | 0.10417 | 5 | 0.4666 + j1.0482
MG4 | 28 | MG4 | 29 | 250 | 0.047348 | 12 | 1.5209 + j0.7521
MG4 | 29 | MG4 | 30 | 175 | 0.033144 | 12 | 1.5209 + j0.7521
MG4 | 30 | MG4 | 31 | 350 | 0.066288 | 12 | 1.5209 + j0.7521
MG4 | 31 | MG4 | 32 | 425 | 0.080492 | 12 | 1.5209 + j0.7521
MG4 | 32 | MG4 | 33 | 325 | 0.061553 | 12 | 1.5209 + j0.7521

## Line Impedence
Configuration | Raa+jXaa | Rab+jXab | Rac+jXac | Rba+jXba | Rbb+jXbb | Rbc+jXbc | Rca+jXca | Rcb+jXcb | Rcc+jXcc
1 | 0.4576 + j1.078 | 0.156 + j0.5017 | 0.1535 + j0.3849 | 0.156 + j0.5017 | 0.4666 + j1.0482 | 0.158 + j0.4236 | 0.1535 + j0.3849 | 0.158 + j0.4236 | 0.4615 + j1.0651
2 | 0.4666 + j1.0482 | 0.158 + j0.4236 | 0.156 + j0.5017 | 0.158 + j0.4236 | 0.4615 + j1.0651 | 0.1535 + j0.3849 | 0.156 + j0.5017 | 0.1535 + j0.3849 | 0.4576 + j1.078
3 | 0.4615 + j1.0651 | 0.1535 + j0.3849 | 0.158 + j0.4236 | 0.1535 + j0.3849 | 0.4576 + j1.078 | 0.156 + j0.5017 | 0.158 + j0.4236 | 0.156 + j0.5017 | 0.4666 + j1.0482
4 | 0.4615 + j1.0651 | 0.158 + j0.4236 | 0.1535 + j0.3849 | 0.158 + j0.4236 | 0.4666 + j1.0482 | 0.156 + j0.5017 | 0.1535 + j0.3849 | 0.156 + j0.5017 | 0.4576 + j1.078
5 | 0.4666 + j1.0482 | 0.156 + j0.5017 | 0.158 + j0.4236 | 0.156 + j0.5017 | 0.4576 + j1.078 | 0.1535 + j0.3849 | 0.158 + j0.4236 | 0.1535 + j0.3849 | 0.4615 + j1.0651
6 | 0.4576 + j1.078 | 0.1535 + j0.3849 | 0.156 + j0.5017 | 0.1535 + j0.3849 | 0.4615 + j1.0651 | 0.158 + j0.4236 | 0.156 + j0.5017 | 0.158 + j0.4236 | 0.4666 + j1.0482
7 | 0.4576 + j1.078 | 0.0 + j0.0 | 0.1535 + j0.3849 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.1535 + j0.3849 | 0.0 + j0.0 | 0.4615 + j1.0651
8 | 0.4576 + j1.078 | 0.1535 + j0.3849 | 0.0 + j0.0 | 0.1535 + j0.3849 | 0.4615 + j1.0651 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0
9 | 1.3292 + j1.3475 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0
10 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 1.3292 + j1.3475 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0
11 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 0.0 + j0.0 | 1.3292 + j1.3475
12 | 1.5209 + j0.7521 | 0.5198 + j0.2775 | 0.4924 + j0.2157 | 0.5198 + j0.2775 | 1.5329 + j0.7162 | 0.5198 + j0.2775 | 0.4924 + j0.2157 | 0.5198 + j0.2775 | 1.5209+j0.7521